M E M O R A N D U M

TO:		Randy Poe, Superintendent

Karen Byrd, Chairperson

Board Members

FROM:	Mike Poiry, Assistant Superintendent

DATE:	August 8, 2019

RE:	Change Order #1 – RA Jones & Collins Underground

Electric BG#19-144

Proposal #1  Additional items required by the electrical

inspector in order to pass final inspection:

- Electric grounding wire from transformers to disconnects

needs to be a #4 copper wire, drawings showed #6.

- Both trailers require an ISB grounding bar which was not

shown on the drawings.

- Each of the 2 new 150 amp breakers installed in the

existing gear require a pad-lockable device which was not

shown on the drawings.  Add - $936.00

Total amount for this change order is $936.00

I recommend the board accept Change Order #1, as presented.