FIELD OBSERVATION REPORT

New West Middle School - Cecilia, KY    					202280 - CA8

Date: February 26, 2025					Time: 12:30 PM

Weather: 50s/ Partly Cloudy

Observed by: Joseph Jones, AIA		Report No:  6

Estimated Completion:  12%

Present on Site:

Kevin Beeler (Wehr Constructors)

East and Westbrook Construction (General Trades), Bailey’s Masonry, Kight’s Plumbing, AES (Electrical), Phillips Brothers (Storm Piping) Withers (Geothermal Well Drillers)

Work in Progress

  - A considerable amount of work had been done despite a very rainy period.

  - Masons had laid the first course of CMUs on the interior footings for most of the building.

  - Footing and stem walls were complete.

  - Plumbers and electricians continued to install under slab utilities.

  - Geothermal well drillers were drilling wells and placing piping in wells.

  - Meetings were held to discuss the installation of concrete slabs to be covered with floor finishes and slabs to have a polished finish.

General Observations

| Item No. | Location | Description/ Correction | Image | Action |
| --- | --- | --- | --- | --- |
|  | Loading Dock Area | Plumbers were installing storm piping near the face of the loading dock. |  | Indicate all below pavement lines on the as-built drawings. |
|  | Geothermal Well Field | The drillers were employing two rigs. |  | Keep drilling logs updated and submit to all parties. |
|  | Area C Kitchen | The northwest corner of the kitchen includes non-food storage, the staff locker room, staff toilet and managers office. |  | Prepare exterior block walls for brick veneer. |
|  | Area C Kitchen | The room with the angled wall is the kitchen managers office. |  | Install outlets are indicated for the managers furniture layout. |
|  | Area C Kitchen | Foreground is the cooking area of the kitchen. |  | Coordinate utilities with the submittals for the cooking equipment. |
|  | Area D | Foreground is the dishwash room looking across to the corridor to the gym/storm shelter. |  | Layout dishwash equipment per the equipment submittals. |
|  | Area D | Group toilets, custodian receiving and the mechanical room are to the left. The exit to the dock is in the center. |  | Install utilities to meet maintenance access requirements. |
|  | Area D Toilet Group | The plumbing serves the fixtures for the student toilets. |  | Plan toilet fixture layouts to comply with ADA requirements and clearances. |
|  | Area D South Corridor | Gym storage and coaches offices are to the left and the art room is to the right. |  | Locate utilities to serve devices and casework along the walls in the rooms. |
|  | Area D Staff Toilets | Under slab plumbing serves the fixtures in these rooms. |  | Install plumbing fixture to meet ADA requirements and clearances. |
|  | Area D West Gym Entrance | This entrance two doors separated by a block pier. |  | Install door frames in compliance with storm shelter requirements. |
|  | Area D Looking West Computer Classroom is to the Left and Group Toilets are to the Right | The walls in this are form the corridor back to the music rooms. |  | Prepare slabs for the respective finishes in this area. |
|  | Area D Vestibule Looking North | The vestibule empties out onto a walk beside the loading dock area. The mechanical room is to the right. |  | Pour slabs at exterior doors to provide full anchorage of the thresholds. |
|  | Technology Computer Classroom Floor Box | The floor box provides data and power connections for the center of the room. |  | Protect floor boxes during construction. |
|  | Area D MDF Room | Walls in this are concrete block. The MDF room is surrounded with block. |  | Plan for data cabling penetrating the MDF walls. |
|  | Area D West Corridor Looking North | Sanitary sewer lines run under the corridor slabs. |  | A third party inspector will verify the slope of the sewer piping under the floor slabs. |
|  | Door Portal at Gym/Storm Shelter | The storm shelter is formed with block intersecting the concrete door portals. |  | Plan for expansion joints at the concrete portals. |
|  | Area A Administrative Area | The footings reflect that the area is surrounded with block construction. The interior is divided by wallboard partitions. The records room is block. |  | Located under slab utilities to feed devices in wallboard partitions. |
|  | Area B Classroom Wing | The first course of block was in place to receive the floor slab. |  | Incorporate the comments from the pre-slab meeting. |
|  | Elevator Pit | The concrete pit walls form the foundation for the elevator shaft. |  | Verify compliance with requirements of the elevator manufacturer. |

- Stored Material:

  - Concrete storm piping and structures and accessories.

  - Concrete accessory materials to construct the foundations and floor slabs.

  - Reinforcing steel and accessories.

  - Crushed stone for pavement areas and back fill for plumbing trenches.

  - Masonry accessories and CMUS.

  - Geothermal piping.

  - Sanitary piping and fittings.

  - Electrical conduits and fittings.

- Follow up items:

  - Keep as-built locations for site utilities up to date on the as-built drawings.

  - Keep as-built locations of mechanical, plumbing, and electrical system locations up to date on the as-built drawings.

  - Correct and address all action items and deficiencies and submit a log to JRA confirming that the work has been completed.

Respectfully submitted,

Joseph Jones, AIA

JRA Architects

Cc: 202280, CA8