Board Memo

DATE:  6/12/2025

AGENDA ITEM DETAILS:

School/Department

Camp Ernst Middle School

Product Vendor or Grant Issuer

Change Order

Product or Grant Name

Change Order #5 for Camp Ernst Middle School, Addition/Renovations, BG 23-269

Date/Term (Beginning and End Dates/Year)

6/12/2025

APPLICABLE BOARD POLICY & STRATEGIC PLAN GOAL:

05.1

Goal 4E: Boone County Schools will provide safe, clean, learner ready facilities. 1. Prioritize the district facilities plan to ensure alignment with the desired state as directed by the strategic plan.

DESCRIBE USE OF CONTRACT/PURCHASE/AGREEMENT

Change Order #5 – This Change Order includes the following:

Proposal 15R2 – Modifying some of the trusses to allow for insulation of the new ductwork. Some of the truss webbing was inadvertently conflicting with some of the new ductwork.

ADD $3,260.00

Proposal 21R- Boone County Maintenance requested removal of all control valves for the building heat pumps.

DEDUCT $5,279.00

Proposal 22BR – Add some custom bent clip plates to allow for anchorage to the unusual profile of the light gauge metal truss.  An additional piece of fabrication was required to provide a secure anchorage point for the specified roof tie-offs.

ADD $2,355.00

Proposal 26R2 – Additional cable tray was needed for installation of the data cabling for the school’s IT Department.  This cable tray was not included in the original contract scope.

ADD $5,581.00

Proposal 31R – Engineer included allowance for a number of fire alarm devices to be relocated for ceiling work during the renovation.  Contractor determined that a lesser number of devices would need to be relocated, resulting in a net credit to the project.

DEDUCT $18,550.00

Proposal 32R – Inspector reviewed installed locations of mechanical equipment disconnects on the mezzanine and nine (9) locations were determined to be non-compliant once all other equipment, ductwork and piping was installed.

ADD $6,923.00

Proposal 34 – Light poles were designed for installation on a typical 277-volt distribution system. However, contractor discovered that this lighting circuit was actually fed from a 480-volt circuit.  The cost is for changing breakers to feed new lighting from a 277-volt circuit.

ADD $7,637.00

Proposal 35R – At two of the classrooms, it was determined that it would be better to build a bulkhead to allow for an extended height of the ceiling rather than keeping the entire ceiling at a consistent elevation.  This gives enhanced headroom and allows the structural members to step the ceiling down in one area.

ADD $6,668.00

Proposal 36 – Two (2) balancing valves were found to be redundant in the mechanical room.  The contractor reviewed this with the Engineer and they were deemed unnecessary for proper system operation.

DEDUCT $15,500.00

Proposal 37 – Light fixtures selected for installation in exterior soffit were found to be undesirable once installed.  Some locations were found not to be feasible for installation of selected fixtures.  New fixtures were selected during construction with Owner and original fixtures were returned/replaced.

ADD $3,759.00

Proposal 38R – M1-M2 light fixtures were called to be surface-mounted but required patching work of the drywall ceiling before installation.  Cost is for general trades work for filling in holes left by existing recess-mounted light fixtures. 
ADD $8,577.00

Proposal 40 – Due to that later completion date to the school year, the same adjustment is being extended to the contractor.

ADD $0.00

FUNDING FOR PURCHASES AND OTHER REQUESTS:

Total Cost

Increase  $5,431.00

$11,518,760.00

Funding Source

Building Fund

*If more than one funding source, list below along with amount or percent for each source

N/A

IF THIS IS A GRANT, ENTER AMOUNT TO BE AWARDED:

RECOMMENDATION:

I recommend the Board approve Change Order #5 for Camp Ernst Middle School, Addition/Renovations, BG 23-269, as presented.

CONTACT PERSON: (submitter)

Kim Best, Assistant Superintendent of Operations